## pressureDrop
Unit conversion of data sheets logaritmic pressure drop curves
Manufacturer | Viessman
Source data sheets | https://vibooks.viessmann.com/de/de
rho_default in kg/m3 | 995.586 |  | dTTra_nominal | 10
from data sheet
[5 empty] | dp=a*x^n |  |  | dp =a*x^2 |  |  | Comparison nominal pressure drop in Pa
Boiler name | data sheet ID | Q_nom | Q_flow_nominal in W |  | dp in mbar x=V_flow in l/h | dp in mbar x=V_flow in m3/h | dp in Pa x=V_flow in m3/s | dp in Pa x=V_flow in m3/s | BESMod AutoparameterBoiler record pressureDrop x=V_flow in m3/s | V_flow_nominal in m3/s | data sheet | x unit conversion with n=2 | BESMod
|  |  |  | n | a
Vitogas 200-F | 5414039 | 12100 | 11000 | 2.033 | 6.477e-06 |  | 13818640707.8097 | 8394140160 | 8744249900 | 0.00026407 | 734.0997 | 585.3568 | 609.7714
|  | 16600 | 15000 | 2.033 | 6.477e-06 |  | 13818640707.8097 | 8394140160 | 8277235400 | 0.0003601 | 1379.1133 | 1088.4734 | 1073.3143
|  | 19900 | 18000 | 2.0226 | 5.2271e-06 |  | 9528873688.7936 | 6774373440 | 7934758100 | 0.00043212 | 1493.5174 | 1264.9496 | 1481.6233
|  | 24300 | 22000 | 2.0226 | 5.2271e-06 |  | 9528873688.7936 | 6774373440 | 7478121700 | 0.00052814 | 2241.198 | 1889.6161 | 2085.9168
|  | 32000 | 29000 | 1.9265 | 7.6403e-06 |  | 3263576367.8053 | 9901776960 | 6679008000 | 0.00069619 | 2699.4267 | 4799.1931 | 3237.1815
|  | 38600 | 35000 | 1.9884 | 3.7095e-06 |  | 4037015758.7956 | 4807473120 | 5994053400 | 0.00084023 | 3093.4303 | 3394.0016 | 4231.7089
|  | 46400 | 42000 | 1.9884 | 3.7095e-06 |  | 4037015758.7956 | 4807473120 | 5184561600 | 0.0010083 | 4445.1529 | 4887.3623 | 5270.7171
|  | 53000 | 48000 | 1.9986 | 2.616e-06 |  | 3316928443.7118 | 3390336000 | 4499607000 | 0.0011523 | 4447.7297 | 4501.7804 | 5974.7006
|  | 66200 | 60000 | 1.9986 | 2.616e-06 |  | 3316928443.7118 | 3390336000 | 3129697800 | 0.0014404 | 6947.3294 | 7034.0318 | 6493.2779
| 5811391 | 78300 | 72000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0017285 | 785.1544 | 726.4851 | 824.5807
|  | 91300 | 84000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0020165 | 1070.1479 | 988.827 | 1122.3459
|  | 104400 | 96000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0023046 | 1399.4045 | 1291.5291 | 1465.9212
|  | 117400 | 108000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0025927 | 1772.9768 | 1634.5915 | 1855.3066
|  | 130400 | 120000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0028808 | 2190.9114 | 2018.0143 | 2290.5019
|  | 143500 | 132000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0031689 | 2653.2499 | 2441.7972 | 2771.5073
|  | 156500 | 144000 | 2.0089 | 1.8763e-07 |  | 278091798.0072 | 243165888 | 276000000 | 0.0034569 | 3160.0301 | 2905.9405 | 3298.3228
Vitocrossal 200 | 5368777 | 82000 | 87000 | 2.1371 |  | 0.21296 | 848079468.8325 | 275996160 | 276000000 | 0.0020886 | 1587.4944 | 1203.9283 | 1203.9451
|  | 108000 | 115000 | 2.1371 |  | 0.21296 | 848079468.8325 | 275996160 | 276000000 | 0.0027608 | 2881.9189 | 2103.5741 | 2103.6033
|  | 134000 | 142000 | 2.1371 |  | 0.21296 | 848079468.8325 | 275996160 | 276000000 | 0.0034089 | 4522.9201 | 3207.2943 | 3207.3389
|  | 175000 | 186000 | 1.9067 |  | 0.070318 | 42455811.2401 | 91131609.6 | 91132000 | 0.0044652 | 1402.3125 | 1816.9962 | 1817.004
|  | 232000 | 246000 | 1.9067 |  | 0.070318 | 42455811.2401 | 91131609.6 | 91132000 | 0.0059056 | 2389.8073 | 3178.3253 | 3178.3389
|  | 293000 | 311000 | 1.9067 |  | 0.070318 | 42455811.2401 | 91131609.6 | 91132000 | 0.007466 | 3736.9319 | 5079.8268 | 5079.8486
| MEAN |  |  | 2.0093

## volume
Volume
Manufacturer | Viessman
Source data sheets | https://vibooks.viessmann.com/de/de
Boiler name | data sheet ID | Q_nom in W | Q_flow_nominal in W | volume in m3
Vitogas 200-F | 5414039 | 12100 | 11000 | 0.0076
|  | 16600 | 15000 | 0.0076
|  | 19900 | 18000 | 0.0097
|  | 24300 | 22000 | 0.0097
|  | 32000 | 29000 | 0.0117
|  | 38600 | 35000 | 0.0138
|  | 46400 | 42000 | 0.0159
|  | 53000 | 48000 | 0.0179
|  | 66200 | 60000 | 0.0219
| 5811391 | 78300 | 72000 | 0.0376
|  | 91300 | 84000 | 0.043
|  | 104400 | 96000 | 0.0483
|  | 117400 | 108000 | 0.0536
|  | 130400 | 120000 | 0.059
|  | 143500 | 132000 | 0.0643
|  | 156500 | 144000 | 0.0696
Vitocrossal 200 (2014) | 5368777 | 82000 | 87000 | 0.229 | due to atypical decreasing volume with increasing power excluded
|  | 108000 | 115000 | 0.225
|  | 134000 | 142000 | 0.221
|  | 175000 | 186000 | 0.306
|  | 232000 | 246000 | 0.292
|  | 293000 | 311000 | 0.279
Vitocrossal 200 (2023) | 5117939 DE | 76000 | 80000 | 0.065
|  | 113000 | 120000 | 0.103
|  | 151000 | 160000 | 0.103
|  | 189000 | 200000 | 0.145
|  | 226000 | 240000 | 0.145
|  | 264000 | 280000 | 0.18
|  | 300000 | 318000 | 0.18